Input / Output Measurement Test:

Reference Documents:

UL 935, 10th edition, Issued: 5/21/01, paragraphs 21.6-21.9, 22.1-22.9, 31.1-31.3

Method:

Ballast tested:

With the device energized at the maximum rated supply voltage and at the rated frequency, the input current and wattage were measured while the ballast was operating the intended lamps as noted in the results. The ballast and the lamps were first operated until the lamps approached normal operating temperature - at least 15 minutes. From the measured values, the power factor was calculated by Input Watts divided by (Input Volts multiplied by Input Amps).

Instructions: Select for autotransformer or isolating transformer magnetic ballasts.

[]For autotransformer type magnetic ballasts, the output voltage was measured between all ballast lead wires or terminals - including the input lead wires or terminals - while in the various modes of lamp and ballast operation noted in the results. The output voltage to ground was measured between all lamp lead wires or terminals and ground while in the various modes of lamp and ballast operation noted in the results. The highest voltage was recorded.

[]For isolating transformer type magnetic ballasts, the output voltage was measured between only between opposite ends of each secondary winding (at lead wires or terminals) - not between isolated secondaries or to the primary - while in the modes of ballast operation noted in the results. The highest voltage was recorded. Voltage to ground was not measured.

[]The maximum starting voltage of an electronic ballast was measured between all lamp lead wires while in the various modes of lamp and ballast operation noted in the results.

For these measurements,

[]The magnetic ballast was tested on the bench.

[]The electronic ballast was placed in a test fixture wireway and the ballast enclosure and test fixture wireway were electrically connected together.

[]The voltage across the power capacitor was measured while in the various modes of lamp and ballast operation noted in the results in order to determine compliance with Section 28 of UL 935.

Results:

Lab Instructions:

For the various modes of lamp and ballast operation find:

[]Using different lamps types and numbers as noted find the maximum input current, input power, and voltage across a power capacitor, if provided,

[]Using a deactivated lamp condition find the maximum input current and voltage across a power capacitor,

[]Using a shorted starter condition to find the maximum input current,

[]Using a no lamp condition find the maximum output voltage.

Record lamp(s) used, and lamp conditions.  Place number in front of lamp conditions that corresponds with data results column.  Cross out lamp conditions that did not apply.

Ballast tested:

The number designation, number of lamps, and lamp conditions below correspond to the columns in the following table:

Four lamps

Three lamps.

Two lamps.

One lamp.

Four lamps, with lamp #1 deactivated/ starter shorted.

Four lamps, with lamp #2 deactivated/ starter shorted.

Four lamps, with lamp #3 deactivated/ starter shorted.

Four lamps, with lamp #4 deactivated/ starter shorted.

Three lamps, with lamp #1 deactivated/ starter shorted.

Three lamps, with lamp #2 deactivated/ starter shorted.

Three lamps, with lamp #3 deactivated/ starter shorted.

Two lamps, with lamp #1 deactivated/ starter shorted.

Two lamps, with lamp #2 deactivated/ starter shorted.

One lamp, with lamp deactivated/ starter shorted.

No load

Ballast tested:

Measurements were made using the following lamp type:

[]Commercially available lamps were used

[]General Electric

[]Philips

[]Osram Sylvania

|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Input Volts (rms) |  |  |  |  |  |  |  |  |
| Input Amps (rms) |  |  |  |  |  |  |  |  |
| Input Watts |  |  |  |  |  |  |  |  |
| Power Factor | 0. | 0. | 0. | 0. | 0. | 0. | 0. | 0. |
| Output Volts (rms) |  |  |  |  |  |  |  |  |
| Measured between leads or terminals | & | & | & | & | & | & | & | & |
| Output Volts (rms) |  |  |  |  |  |  |  |  |
| Measured volts between lead wire or terminal and ground | & | & | & | & | & | & | & | & |
| Maximum Starting Volts (peak) |  |  |  |  |  |  |  |  |
| Capacitor Volts ___ µF |  |  |  |  |  |  |  |  |

[]The measured input current did not exceed 110% of the marked rating.

[]For a ballast marked for use in a portable lamp, the measured voltage did not exceed 150 volts to ground.

[]The measured output voltage or voltage to ground was greater than 300 V which warranted the marking of the output voltage.

[]The measured output voltage was greater than 600 V however, the voltage to ground was less than 600 V.

[]The measured output voltage to ground did not exceed 110% of the marked rating.

Note: If power capacitor was measured here, add result page for Section 31.

Other Observations: